## 2026_Town_Dam_Month-to-Date_Wat
Form Completed By: | Date and Time of Check-In | Hwy 557 Ruler | Dam Ruler (N/A when Logs Out) | Is Water Level In Compliance | OOC Comment | Weather (temperature in celsius) | Water Management Plan Period | Type of Check-In | Bay 1: TURBINES | Bay 2: 6 Logs Maximum | Bay 3: 8 Logs Maximum | Bay 4: 10 Logs Maximum | Bay 5: MECH GATE MAX 9 Logs | Bay 1 After change: TURBINES | Bay 2 After change: 6 Logs Maximum | Bay 3 after change: 8 Logs Maximum | Bay 4 after change: 10 Logs Maximum | Bay 5 after change: MECH GATE MAX 9 Logs | Dam Ruler After Log Changes | WATER TEMPERATURE if required
Dana | 2026-05-30 17:30 | .735 (.73-.75, but settles mostly at .735, same as this AM) |  | NO | Level is in compliance. Just flagging to add additional info. I was going to open the gate slightly to assist with coming into June 1 compliance, but given dry forecast, that Scarfe is closed up, and that the 557 ruler held from this morning, I'll continue to monitor at this time. If level comes up any further I'll open gate at town dam to release a bit more. If it holds, it will likely start to decline on its own and I will permit it to drop into compliance unless forecast changes and we get more rain than currently forecasted. | 22C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Dana | 2026-05-30 09:21 | .74 (.73–.75), will open gate a small amount to assist with decline into compliance change starting tomorrow. Wanted to come in from higher side due to drier forecast and decreased flow from scarfe as Canoe Lake is now recovering to return to compliance now also. Ruler reading to change from yesterday as it was reported at .69 but photo backup showed it was .71 |  | YES |  | 13C, in 14-day forecast 60% chance of 1-3mm on June 4th, 60% chance of ~10mm on June 10th. Small % for remaining days from 10-30% chance each day, but no accumulation noted | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Zoran | 2026-05-29 11:59 |  | 0.71 | YES |  | 22 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | [6 empty] | 12
Zoran | 2026-05-29 09:23 | 0.69 |  | YES |  | 17 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Greg | 2026-05-28 11:44 |  | 69 | YES |  | 14 sunny | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 2 Logs Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out |  | N/A
Zoran | 2026-05-28 09:19 | .68-.69 |  | YES |  | 15 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Colin | 2026-05-27 09:36 |  | 60 | YES |  | 18 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 61 | 14
Dana | 2026-05-27 06:47 | 0.645 |  | NO | In compliance. Flagged to add notes. Will closing gate further today and sealing bays for summer hold. This should level out the water level between dam and 557 rulers, and let it come up a small amount so it is at or close to summer hold max compliance level due for June 1st of .66. | 7C, no rain in next 7 days forecasted | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out
Colin | 2026-05-26 10:49 | Wavy moving 64-66 |  | YES |  | 18 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out
Colin | 2026-05-26 09:27 |  | 58-59 | YES |  | 18 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | #2 ON only = 2 Logs Out | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out | 60 | 14
Colin | 2026-05-25 16:03 |  | 59 | YES |  | 19 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | 59 | 12
Colin | 2026-05-25 15:46 | 66 |  | YES |  | 19 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Zoran | 2026-05-25 11:21 |  | 0.58 | YES |  | 14 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out | [6 empty] | 12
Zoran | 2026-05-25 09:12 | 0.665 |  | YES |  | 12 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Dana | 2026-05-24 19:45 | 0.665 |  | NO | The water level is in compliance - just flagging as out to add notes that can be explained to residents who are concerned about the Duborne level. I went out again to verify the ruler at 557, which is holding. This means we will likely be able to replace additional logs again tomorrow or Tuesday, once we see a decline on the 557 ruler. We cannot drop all 33 logs back in at once, without causing issues as well, so they are replaced in groups each year after freshet based on forecast, incoming flow, current conditions in the basin. There is a taper from Duborne towards the dam while logs are out. As we have approx 2/3 of the dam closed back up, it is a less extreme taper, but still present. Until water recedes from the shoreline by Dawsy bridge (a benchmark location for the lower end of the river), we cannot replace all logs. Above Duborne there are plans to complete another round of log replacement this week provided the current trend continues so we are in line for June compliance levels down the watershed. This includes the Blind River dam as well. We are currently sitting at .665, which is in the compliance levels permitted by the WMP (.60-.76), and is above the target range of the WMP which is .60-.66. With this many logs back in already, we cannot be much higher as once the logs are back in and the level flattens out between the dam ruler and 557, the lower end and west arm of river are accustomed to the target ranges and much higher than target max of .66 with all logs in causes water up on shorelines in low lying areas in these locations. Our goal is to be above June compliance slightly as we approach June 1, so we can be at the maximum height for summer to begin (June 1-Sep 30 compliance and target range is .60-.66). | 8C, raining | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Zoran | 2026-05-24 08:56 | 0.665 |  | YES |  | 9 degrees; 2-6mm possible today and no rain accumulation forecasted over next 14 days / ds | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Zoran | 2026-05-23 10:09 |  | 0.57 | YES |  | 15 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out | 0.56
Zoran | 2026-05-23 08:50 | 0.655 |  | YES |  | 7 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out
Zoran | 2026-05-22 15:59 | 0.61 |  | YES |  | 16 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out
Zoran | 2026-05-22 11:28 |  | .38-.39 | NO | Monitoring return to compliance and for further log drops to close up the dam. | 15 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX) | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | 0.46
Zoran | 2026-05-22 09:25 | .59-.595 |  | NO | Monitoring return to compliance and for further log drops to close up the dam. | 14 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX)
Dana | 2026-05-21 16:48 | .595 (.5925-.6) |  | NO | Monitoring after log adjustments today for return to compliance, and for planning next adjustments (to further close dam up). Log drops at both Matinenda and Chiblow today that will be felt down below in the upcoming days. | 16C, minimal rain in 14-day forecast (see pics) | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX)
Colin | 2026-05-21 15:25 | 59 |  | NO | Monitoring return to compliance after log drop | 15 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX)
Zoran | 2026-05-21 14:31 | .595-.60 |  | NO | Monitoring return to compliance after log drop. | 13 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX)
Zoran | 2026-05-21 11:07 | 0.59 |  | NO | Will be dropping logs to return to compliance, and additional as Matinenda starting to close up today also/ds. | 10 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 3 Logs Out
Colin | 2026-05-21 11:01 |  | 31 | NO | Will be dropping logs to return to compliance, and additional as Matinenda starting to close up today also/ds. | 16 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 3 Logs Out | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 9 Logs Out (MAX) | 35 | 11
Zoran | 2026-05-21 09:14 | 0.595 |  | NO | Will be dropping logs to return to compliance, and additional as Matinenda starting to close up today also/ds. | 8 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 3 Logs Out
Zoran | 2026-05-20 11:10 |  | .21-.25 | NO |  | 10 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 3 Logs Out | 0.29 | 8
Colin | 2026-05-19 13:26 |  |  | YES |  |  | Apr. 1 to May 31 *Take Water Temp* | ONSITE only Powerhouse | NO LOGS OUT = Both Off | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | 28
Zoran | 2026-05-19 11:18 |  | .25-.29 | YES |  | 14 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | [6 empty] | 6
Colin | 2026-05-16 08:02 |  | Moving 23-26 | YES |  | 11 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | [6 empty] | 7
Colin | 2026-05-16 07:47 | 62 |  | YES |  | 11 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out
Zoran | 2026-05-15 15:01 |  | 0.07(0.04-0.1) | YES |  | 14 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX) | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out | 0.2 | 8
Colin | 2026-05-14 11:04 | 63-64 more to 64 |  | YES |  | 16 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Colin | 2026-05-13 11:23 | 65 |  | YES |  | 8 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Dana | 2026-05-13 07:10 | .655-.66, in upper target range within compliance. First round of logs back in dam. Monitoring rain to begin next round of drops, possibly before weekend. |  | YES |  | 4C, steady rain continues from overnight. 80% 1-3mm this morning; 70% ~1mm this afternoon. 40% <1mm this evening. 10-20% chance overnight and tomorrow. 30% chance FRI. 80% ~5mm SAT. 40% ~1mm SUN. 70% ~15mm MON. 60% 1-3mm TUE. | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Colin | 2026-05-12 14:54 | 65-66 |  | YES |  | 8 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Dana | 2026-05-12 08:38 | .665 (.66-.67) |  | NO | Ruler is actually in compliance. Flagged as no to add remarks to include our plans for rain so river residents can be updated should they ask. As most logs remain out of the dam at this time, we will continue to monitor before dropping more logs to see how much of the forecasted rains we receive before adding more logs, unless needed. This means we will lean more on the mech gate operation until they are replaced, which is currently wide open. As we add logs and close gate, river residents will see the water level off in front of their house until it begins to taper again towards the dam, and will continue this cycle after we add logs each time, until they are almost all replaced when the taper towards the dam becomes less noticeable on their water front. We are well within compliance at this time, and are almost in the target range. | 6C. Forecasting 90% of ~16mm rain today including overnight, FRI 60% ~5mm, SUN 70% 15-20mm, MON 80% 20-25mm | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Zoran | 2026-05-11 11:36 | .68 (.67-.69) |  | YES |  | 9 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 4 Logs Out
Dana | 2026-05-11 07:05 | .69 (.685-.685) |  | YES |  | -3C, forecasting lots of rain over next 5 days (see pic). Includes 90% at 10-15mm tomorrow and 70% ~5mm Wednesday. | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 4 Logs Out
Zoran | 2026-05-10 10:20 | .715-.735 |  | YES |  | 10 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 4 Logs Out
Zoran | 2026-05-09 10:18 |  | Bellow the mark | NO | Continued decline observed at 557. Expect to be in compliance tomorrow, dropping logs by early next week pending forecast. (DS) | 9 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 4 Logs Out | 0.02-0.11
Zoran | 2026-05-09 08:37 | .77(.765-.775) |  | NO | Continued decline observed at 557. Expect to be in compliance tomorrow, dropping logs by early next week pending forecast. (DS) | 10 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-08 15:36 | .80-.81 |  | NO | Continued decline with gate back open, likely back in compliance tomorrow, with gate adjustment Saturday or Sunday to begin slowing things down ahead of log drops next week. Potomac appears back down to its normal or almost normal levels. Measured drop from high water there is over 4' or 120cm back down to its current state from where it was during flood contribution. | 15C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Greg | 2026-05-08 10:45 | 82 |  | NO | Continued decline observed at 557. Expect to be in compliance over the weekend, or early next week. | 11 sunny | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Greg | 2026-05-08 09:43 |  | N/A under ruler | NO | Continued decline observed at 557. Expect to be in compliance over the weekend, or early next week. (DS) | 7 sunny | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 6
Dana | 2026-05-08 06:28 | .83 (.82-.84) |  | NO | Continued decline observed. As bay 5 is opened fully again with most of the debris that had accumulated removed, the decline from yesterday is a larger amount as our output to Huron has increased again (outputting more than before the MNR work on Bay 5, as the debris was restricting some flow also. It is great they were able to remove it in a timely manner to continue decline in level). Currently expect to be in compliance by early next week, possibly as early as Sunday, and nearing our target levels shortly after that next week. If we stay on trend, we may slowly start to replace logs early next week to slow the decline down as we approach the target range for June to September of 6cm (.60-.66 mStaff). While rain is forecasted over the next 5 days, current forecasted amounts are not expected to stop the decline here, but may slow the amount of decrease observed if we get all of it. This opinion is fluid and will change as the forecast changes as well. Currently forecasting 40% <1mm tonight; 70% 2-4mm tomorrow; 40% ~1mm Sun, Mon, Tue and Wed. All logs remain out of dam. | -1C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-07 14:54 |  | 0.35 | NO | All logs out of dam again and most of the debris is removed from Bay 5 (the gigantic stump from upstream in the river). We will continue to monitor decline into compliance (.76 is max) and then begin to close up dam to move into target range as water levels permit. Will keep an eye for additional debris and as we get dam closed back up more, will contact MNR to continue with removal of remaining debris in dam. | 10C | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | Below ruler to .00 | NA
Dana | 2026-05-07 13:46 | .88 (.87-.8875; windy) |  | NO | Possibly a small decline or hold observed at 557. Decline slowed as MNR work underway at town dam in Bay 5 to clear debris restricting flow. Some River residents may notice water levels temporarily held/increased while work underway to clear debris in Bay 5, but will lower once Bay 5 is back in service as water level draw (taper) towards dam increases again. TBR currently requests that work coordination efforts be sent via email to PW supervisor. Contacting the PW on call number may not get the correct PW individual. I will notify MNR of same so they can liaison directly on a go forward. NSPG details will continue to come via email in the report you're reading this in, unless urgent or following up to a report as was done earlier in freshet. Thank you. | 10C, windy | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED
Dana | 2026-05-07 11:26 | .885 (.88–.89) |  | NO | Slower decline but still trending down. MNR work continues in bay 5 at town dam to remove gigantic stump from upstream on river. TBR and MNR met onsite this AM to discuss. Did not require excavator assistance at that time. | 7C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED
Dana | 2026-05-07 05:25 | .89 (.885-.895) |  | NO | Continued decline observed at 557. Decline slowed as MNR work underway at town dam in Bay 5 to clear debris restricting flow. Some River residents may notice water levels temporarily held/increased while work underway to clear debris in Bay 5, but will lower once Bay 5 is back in service as water level draw (taper) towards dam increases again, as Bay 5 outflow from dam returns to its max potential on completion of work. . | -1C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED
Kevin | 2026-05-06 15:40 | 0.9 |  | NO | See Dana's earlier comments for details. | 7 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-06 12:49 | .90 (.89-.91) |  | NO | Continued decline observed at 557, temporary closure of bay 5 gate while MNR tries to clear debris lodged in gain to increase outflow from dam. | 7C, light snow | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED
Colin | 2026-05-06 09:13 |  | Moving below zero to 3 | NO | Continued decline observed. See Dana's comments today for additional info. | 7 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 6
Dana | 2026-05-06 07:30 | .91 (.905-.915) |  | NO | Continued decline observed. Trending towards compliance of .76. Still water moving down from above on WMP, but keeping ahead of incoming water to continue decline. Upstream slowly declining as well, and Potomac output back near normal level range from earlier extreme flood conditions. | -1C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-06 03:45 |  | .34 (.31-.36) | NO | Level rising at town dam as mechanical gate closed (equivalent of 9 logs back in) while MNR working to clear debris from it. See more details in work log. Lower end of the river will go up while gate closed also. Will monitor 557 for over all decline in the basin on a go forward, but it will likely slow during the work. The taper to the dam sill will increase again once the gate is opened again, hopefully with the debris removed. (MNR looking to continue delimbing or remove via excavator from shore, will need TBR approval for shoreline access also). Gain Cover on bay 5 left off while stump suspended so added flag tape and open hole signs to dam deck to avoid anyone falling in. Looking to get bay 5 opened back up fully as soon as possible. | NA | Apr. 1 to May 31 *Take Water Temp* | ONSITE only Headpond | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | NO LOGS OUT - GATE CLOSED | [6 empty] | NA
Greg | 2026-05-05 12:28 | .94-.95 |  | NO | Continued decline observed. See Dana's comments from prior check for more detail. | 9 overcast breezy | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Zoran | 2026-05-05 09:10 |  | 0.03-0.11 | NO | Continued decline observed. See Dana's notes for more detail. | 6 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 8
Dana | 2026-05-05 07:50 |  | .07 (.03-.11 - turbulent) | NO | See 557 comments. Please also note unit 1 has also passed water throughout freshet but we cannot flag it as online so it doesn't show on report. We've logged it on our website as .25 but it is passing more than that for flow. 100 year flood planning shows that 4 bays can pass the amount of water needed in that scenario, so having the turbines releasing extra water this season was above that calculation. The turbines don't typically run during freshet due to turbulence and low head pressure, however both passed water this season in addition to all logs out of dam (which means mechanical gate equivalent fully opened also). | 4C | Apr. 1 to May 31 *Take Water Temp* | ONSITE only Headpond | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | Will check later
Dana | 2026-05-05 07:00 | .97 (.955-.99), upstream and downstream rulers vary by 1-2cm as downstream is subject to more current as the water hits the ruler head on, while upstream is protected. Using upstream as usual. |  | NO | Observed continued decline. Entire WMP watershed is declining slowly as well. Water Level Reading is back on the mstaff gauge. MNR will install a second ruler above existing this year. Matinenda and Canoe Lake above are in compliance, but remain over target levels (WMP). Chiblow and Duborne slowly working their way down to compliance and will continue to be monitored for further decline. All logs (and equivalent) remain out of Town Dam. As level continues to drop, and with contribution from Potomac reducing by so much, the River and West arm of the River will begin to see the normal water taper towards the dam (low water temporarily while dam is wide open and drawing freshet water from Duborne). This will be temporary low water for the affected residents, and will level out once the dam is closed back up after water flow and levels stabilize for Duborne. | 4C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Greg | 2026-05-04 15:11 |  | Fluctuating between.03-13 | NO | High water levels during freshet | 12 overcast | Apr. 1 to May 31 *Take Water Temp* | ONSITE only Headpond | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | N/A
Dana | 2026-05-04 13:30 | 1.03, almost back on gauge (ruler) |  | NO | Observed continuing decline. All logs remain out of dam. Bay 5 debris will be looked at Wednesday by MNR for removal or removal plan. | 13C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Zoran | 2026-05-04 09:07 |  | 0.07-0.14 | NO | Continued decline observed. See Dana's notes for more detail. | 6 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 7
Dana | 2026-05-04 06:45 | 1.04-1.05, almost back on mstaff gauge. |  | NO | Continued decline. All logs remain out of dam. Declining levels observed upstream as well again, but levels still higher than targets above also. Forecast is favourable for continued decline over the next 5 days, with no to minimal rain, and cooler overnight temps. | 3C, fog advisory | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-03 09:00 | 1.08 |  | NO | Continued decline, along with upstream levels as well. All logs remain out. | 6C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-02 08:45 | 1.11 |  | NO | Continued decline, following trend from upstream where levels are also declining. All logs remain out of dam. | 4C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Dana | 2026-05-01 11:20 | 1.15-1.16, declining |  | NO | Declining from peak observed overnight. Monitoring to see when we can drop above again in coordination with MNR. Despite drop above yesterday, above levels showing continued decline also, which is a good indicator freshet levels are beginning to slow. Will need to monitor forecast closely for rain also. | 3C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Colin | 2026-05-01 09:33 |  | Moving 20-26, holding, or reduced increase | NO | Freshet. TBR, MNR and MFN aware | 5 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 6
Dana | 2026-05-01 01:00 | 1.17 |  | NO | Should peak shortly after rain received on 28th as upstream beginning to show signs of peak/trending back down. Coordinating upstream log drops as levels stabilize and begin to decline above also to assist below. First series dropped Thursday, and levels above showed continued decline afterwards, which is a good sign of things beginning to slow. All logs remain out. | 0C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX)
Colin | 2026-04-30 15:29 |  | Moving 25-30 | NO | Freshet. TBR, MNR and MFN aware | 11 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | 25-30 | 7
Zoran | 2026-04-30 13:40 |  | .24-.35, still climbing since rain overnight on 28th | NO | Freshet. TBR, MNR and MFN aware | 11 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 7
Colin | 2026-04-29 10:50 |  | Moving 19-24, rising from rain received yesterday. | NO | Freshet. TBR, MNR and MFN aware | 8 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 7
Colin | 2026-04-28 09:19 |  | Moving 17-21 | NO | Freshet. TBR, MNR and MFN aware | 10 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 9 Logs Out (MAX) | [6 empty] | 7