# DUNDALK SANITARY SEWAGE COLLECTION SYSTEM

# 2025 Annual Performance Report 110-W601

May 2026

Prepared by: The Township of Southgate

##### TABLE OF CONTENTS

Introduction	4

Background	4

System Description	5

System Summary	5

  - Monitoring Data & Interpretation	5

  - Operational Problems & Corrective Actions	6

  - Calibration, Maintenance & Repairs	6

  - Complaints & Actions Taken	6

  - Alterations to the Authorized System	6

  - Overflows & Spills	7

  - Reduction Efforts (Overflows, Spills)	7

- Closing	7

LIST OF APPENDICES

### Appendix A – Sanitary Infrastructure Map

# Introduction

This report has been prepared by the Township of Southgate to satisfy the requirements of Schedule E, Section 4.6 of the Environmental Compliance Approval for a Municipal Sewage Collection System that has been issued to the Township of Southgate by the Ontario Ministry of Environment, Conservation and Parks (MECP).

# The report covers the period from January 1 to December 31, 2025, for the following municipally owned         and operated wastewater collection system:

# Wastewater Collection System Information

# Consolidated Linear Infrastructure – Environmental Compliance Approval (CLI-ECA_

# ECA Number:		110-W601

# Issue Number:		1

# Issue Date:		March 2, 2023

# Background

An Operations and Maintenance (O&M) Manual dated June 2023, has been prepared for the Authorized System, in accordance with Schedule E, Condition 3.2 of the CLI ECA No. 110-W601, Issue No. 1. Consistent with Schedule E, Condition 3.2 of the CLI ECA for the System, the objective of the operation and maintenance of the System is to protect sources of drinking water, such as those included in the Standard Operating Policy for Sewage Works, and any applicable local Source Protection Plan policies.

The information, photographs, interpretations, maintenance records, etc. collected in accordance with the O&M Manual are to be compiled into the Performance Report for the System and submitted to the MECP Director on or before March 31st of each calendar year, covering the period from January 1st to December 31st of the preceding calendar year. Consistent with the CLI ECA for the Township’s System, each Performance Report shall contain, but not be limited to, the following:

- Summary of all monitoring data, as well as an interpretation of the data and any conclusions drawn from the data evaluations about the need for future modifications to the System or system operations.

- Summary of operating problems and corrective actions taken.

- Summary of all calibration, maintenance, and repairs carried out on any major structure, Equipment, apparatus, mechanism, or thing forming part of the System.

- Summary of complaints related to the System and the steps taken to address the complaints.

- Summary of Alterations to the System including a list of Alterations that pose a significant Drinking Water Threat.

- Summary of system overflows and spills within the Collection System.

- Summary of the efforts made to reduce Collection System Overflows, Spills, STP Overflows, and/or STP Bypasses.

The Performance Reports for the System can be viewed at the following location:

  - Electronic copy format at https://www.southgate.ca/

# System Description

The Township’s Sanitary Collection System (System) is composed of the Dundalk sanitary collection system within the urban boundary of Dundalk.

The System is designed to convey sanitary sewage and consists of a combination of sanitary sewers, maintenance holes and a Township operated sewage pumping station.

# System Summary

## Monitoring Data & Interpretation

| Month | Total Flow | Average Day Flow m3 | Max Flow m3 |
| --- | --- | --- | --- |
| January | 45366 | 1463 | 2655 |
| February | 30187 | 1078 | 1438 |
| March | 98201 | 3168 | 6595 |
| April | 72770 | 2426 | 7827 |
| May | 39432 | 1272 | 1685 |
| June | 31800 | 1060 | 1292 |
| July | 29421 | 949 | 1361 |
| August | 24614 | 794 | 1021 |
| September | 21711 | 724 | 864 |
| October | 22045 | 711 | 775 |
| November | 30683 | 1023 | 1521 |
| December | 40591 | 1309 | 2422 |
| Total / Year | 486821 | 1331 | 7827 |

## Operational Problems & Corrective Actions

There were no known operating problems encountered regarding the Township System during Calendar Year 2025.

## Calibration, Maintenance & Repairs.

During the year 2025, the Township continued its regular maintenance program including regular inspection and cleaning of sewers and maintenance holes on an as-needed basis.  The inlet structure for Cell 1 was cleaned out using a vac truck.  The structure between Cells 3 and 4 was cleaned out using the vac trailer.  There was a thick, sludge-like matter in the structure.  The foot valve on the Jet pump was replaced. Calibration of the influent and effluent flow meters was completed in October 2025 by a third party.  Calibration of the TSS and DO analyzer probes were completed by Southgate staff in January and July.  Handheld calibration by a third party on February 3, 2025.  Both blowers received oil changes and visual inspection.

## Complaints & Actions Taken

There were 3 complaints in 2025. All were related to sewage backing up.

February 26, 2025 – A previous repair of the sanitary service at property line had become dislodged causing a blockage.  A vac truck exposed the piping.  A plumber cleared the blockage.  The vac truck flushed the service and the main.  The plumber repaired the piping.

July 10, 2026 – Dumping station backing up.  Vac truck called in to flush and camera.  Flushing was unsuccessful.  Upon camera investigation, a rock was found jammed in the piping.  Vac truck exposed the piping.  Southgate staff cut out a section of piping, removed the rock and repaired the piping.

December 18, 2025 – Sewer back up.  Plumber on-site.  Plumber had removed half a garbage bag of flushable wipes from the sanitary service.  Upon investigation, found the manhole full of flushable wipes causing a blockage.  A vac truck was called in, cleaned the manhole and flushed the sewer main.  Plumber cleared the sanitary service and took a video of the cleared service.

## 4.5	Alterations to the Authorized System

- Within the System the following sewers are currently owned and operated by the developer under the existing ECA Number 0612-C35HWP.

Flato Developments East Phases 7, 8, and 10 (Existing ECA 0612-C35HWP)

  - 1,367 m = 200mm diameter.

  - 287 m = 250mm diameter.

Within the above noted Phases, there is also a sewage pumping station that has been included. Director Notification was previously submitted.

- Within the System the following sewers are currently under construction and will be owned by the developer. Director notification will be provided under separate cover.

Flato Developments East Phase 11

  - 513m = 200mm diameter

- Within the System the following sewers are currently under construction and will be owned by the developer. Director notification will be provided under separate cover.

White Rose Phase 3

  - 520m = 200mm diameter.

## Overflows & Spills

There were no known overflows or spills within the System within the 2025 Calendar Year.

## Reduction Efforts (Overflows, Spills)

Within the 2025 Calendar Year the Township prepared and implemented the emergency discharge plan for the Dundalk Wastewater Treatment Facility (WWTF).

Additionally, the Township continues to prepare and issue the annual Reserve Capacity Calculations for The Dundalk WWTF to ensure that treatment capacity is maintained and achieves the PPCP. The Reserve Capacity Calculations are publicly reported and adopted through Council.

# Closing:

The above Annual Performance Report is respectfully Submitted by Township of Southgate.

Cory Henry – Public Works Manger – Water Operations

Reviewed by the Township of Southgate

MCKENZIEST.

T.

SWMF

ST

STREETB

TODD CR.

BRAD EX

STREET D

OPEN SPACE

TOWNSHIP OF SOUTHGATE

FENNELLST.

AITCHISONAVE.

STREET C

STREET B

WETLANDBUFFER

WETLANDLIMIT

SIGNIFICANTW  H

WETLAND

STREET A

MIDDLETONST.

CORBETTST.

DOCL

SWMF

SWMF

DOYLE ST.

WILSON CRT.

SWMF

GLENELG ST.

BRADLEY ST.

AVE.

PINE CRT.

GREY ST.

HIGHPOINT ST.

DUNDALK FIRE DEPARTMENT

DUNDALK ST.

KING'S HIGHWAY No. 10

TORONTO ST.

McGREGOR CRT.

OSPREY ST.

PROTON ST.

KEPPEL (ROW)

IDA ST.

BRAEMORE ST. W.

BRAEMORE ST. E.

D4 WATER TOWER

MACDOWELL ST.

MILL ST.

WELL D4

HIGH POINT

PROTON ST.

PUBLIC SCHOOL

OWEN SOUND ST.

HOLLAND ST.

ARENA

LEGEND:

McAULEY (ROW)

SINCLAIR ST.

MAIN ST. WEST

YOUNG ST.

ALICE ST.

VICTORIA ST.

MAIN ST. EAST

McAULEY ST.

RUSSEL ST.

SHEFFIELD ST.

ARTEMESIA ST.

PROPERTY

MANHOLES

TOWNSHIP OF SOUTHGATE BOUNDARY EXISTING PROPERTY LINE

PROPOSED DEVELOPMENT PARCELS WATERCOURSES

WETLAND (GRCA)

SANITARY MANHOLE

MUNICIPALLY OWNED MANHOLE NUMBER

MANHOLE NOT YET ADOPTED BY MUNICIPALITY

HANBURY ST.

WELL D3

HAGAN ST.

RUSSELL ST.

GOLD ST.

ROWE'S LN

HAGAN STREET

NIXON ST.

WERRY AVE.	RIDLEY CR.

ELM ST.

SEWER SIZE (N/A TO WWTF)

200mm Ø 250mm Ø 300mm Ø 375mm Ø 450mm Ø 525mm Ø 600mm Ø

MORROW CIR.

BELL CIR.

15.25m EASEMENT

WERRY AVE.

SEELEY AVE.

RIDLEY CR.

SANITARY PUMPING STATION

PROTON COMMUNITY SCHOOL

WELL D5

ELM ST.

VANDUSEN AVENUE

MOODY STREET

MOODYST.

RUSSELLST.

VANDUSEN AVENUE

STOCKSAVE.

PARK

VAND  AVE.

SPS

COLGANCRES.

PIPE MATERIAL

ASBESTOS CEMENT CONCRETE

POLYVINYL CHLORIDE

MATERIAL

FLOW DIRECTION

COLOUR CODED DIAMETER

SLOPE LENGTH

IN-LINE CLEAN OUT AND SHUT-OFF VALVE

WRIGHTAVE.

RUSSELLST.

SYMINGTONST.

MORGANAVE.

FORCEMAIN

SWMF

SWMF

IDA ST.

SWMF

MILLNERAVE.

MCALLISTERST.

MILLINERAVE.

COMMERCIAL DEVELOPMENT

ECO-PARKWAY

150Ø PVC SDR 26 SERIES 160 FILTER WASTE PUMP DISCHARGE

ACCESS ROAD

FILTER WASTE RETURN

MANHOLE T-2 APPROX. LOCATION

BOTTOM OF BANK

INFLUENT CHAMBER

CHEMICAL STORAGE FACILITIES (ALUM STORAGE)

BYPASS

CHEMICAL

METER BUILDING

RAW SEWAGE PUMPING STATION

150Ø PVC SDR 26

250Ø A.C. TO M.H. T-1 MANHOLE T-1

APPROX. LOCATION

INLET

BYPASS

100Ø SCH 80 CPVC AIRMAIN

c/w TRACER WIRE

BLOWER

CONTROL STRUCTURE 2 APPROX. LOCATION

BYPASS

INLET APPROX. LOCATION

300Ø OVERFLOW

300Ø D.I.

SERIES 160 FILTER WASTE PUMP DISCHARGE

APPROX. LOCATION 250Ø P.E.

BUILDING

CELL No.4

CELL No.3

RAW SEWAGE

FORCEMAIN

NORMAL OPERTING WATER LEVEL: 506.45DUNDALK LANGOORMOANL SOPERTING WATER LEVEL: 506.47

BOTTOM OF CELL: 504.67 VOLUME: 46,660 m3

BOTTOM OF CELL: 504.67 VOLUME: 46,660 m3

POST AERATION CELL

FILTER BUILDING

CONTROL STRUCTURE 8 (OVERFLOW)

APPROX. LOCATION

CELL 4 INLET APPROX. LOCATION

CONTROL STRUCTURE 7 APPROX. LOCATION

BOTTOM OF BANK

CELL 3 INLET APPROX. LOCATION

NOTES:

This is a schematic representation of the sanitary sewer

400Ø EMERGENCY

300Ø CELL No.4

400Ø CELL No.3

300Ø CELL No.3

450Ø PVC SDR 35 FILTER EFFLUENT

500Ø P.E. EFFLUENT

OVERFLOW

500Ø P.E.

FILTER BY-PASS

INFLUENT

BOTTOM OF BANK

CONTROL STRUCTURE 3 APPROX. LOCATION

EFFLUENT

BOTTOM OF BANK

300Ø CELL No.3 INFLUENT

MANHOLE No.1 APPROX. LOCATION

INFLUENT

BYPASS CONTROL STRUCTURE APPROX. LOCATION

BYPASS

CONTROL STRUCTURE 6 APPROX. LOCATION

collection system. While this drawing and its detail views are shown to a scale, symbols and sanitary sewers are not plotted to

scale. This mapping should be used for general reference purposes only.

CONTROL STRUCTURE 1

300Ø CELL No.2

BOTTOM OF BANK

BOTTOM OF BANK

CELL 1 INLET

(OVERFLOW)

APPROX. LOCATION

EFFLUENT

CELL 1 INLET APPROX. LOCATION

CONTROL STRUCTURE 5

APPROX. LOCATION

CONTROL STRUCTURE 4 APPROX. LOCATION

CELL No.2

APPROX. LOCATION

LAGOONS

CELL No.1

WASTEWATER TREATMENT FACILITY

NORMAL OPERTING WATER LEVEL: 507.96 BOTTOM OF CELL: 506.15

DUNDALK

NORMAL OPERTING WATER LEVEL: 509.30 BOTTOM OF CELL: 507.50

FUTUREROW

VOLUME: 57,600 m3	VOLUME: 57,600 m3

BOTTOM OF BANK

BOTTOM OF BANK

#### DUNDALK SANITARY COLLECTION SYSTEM